## Foot-mounted frames, IM B3
IEC motor frame sizes — Foot-mounted frames, IM B3 — all dimensions in mm
Frame | H | A | B | C | K | D×E | D×E 2p | kW 2p | kW 4p
63 | 63 | 100 | 80 | 40 | 7 | 11×23 | = | 0.18–0.25 | 0.12–0.18
71 | 71 | 112 | 90 | 45 | 7 | 14×30 | = | 0.37–0.55 | 0.25–0.37
80 | 80 | 125 | 100 | 50 | 10 | 19×40 | = | 0.75–1.1 | 0.55–0.75
90S | 90 | 140 | 100 | 56 | 10 | 24×50 | = | 1.5 | 1.1
90L | 90 | 140 | 125 | 56 | 10 | 24×50 | = | 2.2 | 1.5
100L | 100 | 160 | 140 | 63 | 12 | 28×60 | = | 3 | 2.2–3
112M | 112 | 190 | 140 | 70 | 12 | 28×60 | = | 4 | 4
132S | 132 | 216 | 140 | 89 | 12 | 38×80 | = | 5.5–7.5 | 5.5
132M | 132 | 216 | 178 | 89 | 12 | 38×80 | = | — | 7.5
160M | 160 | 254 | 210 | 108 | 15 | 42×110 | = | 11–15 | 11
160L | 160 | 254 | 254 | 108 | 15 | 42×110 | = | 18.5 | 15
180M | 180 | 279 | 241 | 121 | 15 | 48×110 | = | 22 | 18.5
180L | 180 | 279 | 279 | 121 | 15 | 48×110 | = | — | 22
200L | 200 | 318 | 305 | 133 | 19 | 55×110 | = | 30–37 | 30
225S | 225 | 356 | 286 | 149 | 19 | 60×140 | = | — | 37
225M | 225 | 356 | 311 | 149 | 19 | 60×140 | 55×110 | 45 | 45
250M | 250 | 406 | 349 | 168 | 24 | 65×140 | 60×140 | 55 | 55
280S | 280 | 457 | 368 | 190 | 24 | 75×140 | 65×140 | 75 | 75
280M | 280 | 457 | 419 | 190 | 24 | 75×140 | 65×140 | 90 | 90
315S | 315 | 508 | 406 | 216 | 28 | 80×170 | 65×140 | 110 | 110
315M | 315 | 508 | 457 | 216 | 28 | 80×170 | 65×140 | 132 | 132
315L | 315 | 508 | 508 | 216 | 28 | 80×170 | 65×140 | 160–200 | 160–200
355M | 355 | 610 | 560 | 254 | 28 | 100×210 | 75×140 | 250 | 250
355L | 355 | 610 | 630 | 254 | 28 | 100×210 | 75×140 | 315 | 315
Dimensions to IEC 60072-1; kW per frame is the usual EN 50347 assignment at 50 Hz, and a high-efficiency motor can be one frame larger. The maker's dimension drawing wins over this sheet. Source: https://tililt.com/charts/iec-motor-frame-chart/

## Mounting codes
IEC motor frame sizes — Mounting codes (IEC 60034-7)
Code | Mounting
B3 | Feet, horizontal shaft
B5 | Large flange (FF), through holes, no feet
B14 | Small face flange (FT), tapped holes, no feet
B35 | Feet and B5 flange
B34 | Feet and B14 face
V1 | B5 flange, shaft down
V5 | Feet on a wall, shaft down
Dimensions to IEC 60072-1; kW per frame is the usual EN 50347 assignment at 50 Hz, and a high-efficiency motor can be one frame larger. The maker's dimension drawing wins over this sheet. Source: https://tililt.com/charts/iec-motor-frame-chart/