## NEC 430.250
Motor full-load current & cable — NEC 430.250 — three-phase full-load amps, and copper AWG
HP | 208 V | 230 V | 460 V | 575 V | Cu 230 V | Cu 460 V
1/2 | 2.4 | 2.2 | 1.1 | 0.9 | 14 | 14
3/4 | 3.5 | 3.2 | 1.6 | 1.3 | 14 | 14
1 | 4.6 | 4.2 | 2.1 | 1.7 | 14 | 14
1-1/2 | 6.6 | 6 | 3 | 2.4 | 14 | 14
2 | 7.5 | 6.8 | 3.4 | 2.7 | 14 | 14
3 | 10.6 | 9.6 | 4.8 | 3.9 | 14 | 14
5 | 16.7 | 15.2 | 7.6 | 6.1 | 14 | 14
7-1/2 | 24.2 | 22 | 11 | 9 | 10 | 14
10 | 30.8 | 28 | 14 | 11 | 10 | 14
15 | 46.2 | 42 | 21 | 17 | 6 | 10
20 | 59.4 | 54 | 27 | 22 | 4 | 10
25 | 74.8 | 68 | 34 | 27 | 4 | 8
30 | 88 | 80 | 40 | 32 | 3 | 8
40 | 114 | 104 | 52 | 41 | 1 | 6
50 | 143 | 130 | 65 | 52 | 2/0 | 4
60 | 169 | 154 | 77 | 62 | 3/0 | 3
75 | 211 | 192 | 96 | 77 | 250k | 1
100 | 273 | 248 | 124 | 99 | 350k | 2/0
125 | 343 | 312 | 156 | 125 | 2×3/0 | 3/0
150 | 396 | 360 | 180 | 144 | 2×4/0 | 4/0
200 | 528 | 480 | 240 | 192 | 2×350k | 350k
250 | — | — | 302 | 242 | — | 500k
300 | — | — | 361 | 289 | — | 2×4/0
350 | — | — | 414 | 336 | — | 2×300k
400 | — | — | 477 | 382 | — | 2×350k
500 | — | — | 590 | 472 | — | 2×500k
NEC table currents are for sizing conductors, fuses and breakers (430.6); set the overload relay from the nameplate. Cable sizes ignore voltage drop, grouping and ambient — check long runs with the voltage drop calculator and your local code. Source: https://tililt.com/charts/motor-current-chart/

## IEC
Motor full-load current & cable — IEC — typical amps, 4-pole IE3, 50 Hz
kW | HP | 400 V | 230 V
0.37 | 0.5 | 1 | 1.7
0.55 | 0.7 | 1.4 | 2.4
0.75 | 1 | 1.7 | 2.9
1.1 | 1.5 | 2.4 | 4.2
1.5 | 2 | 3.3 | 5.7
2.2 | 3 | 4.6 | 8
3 | 4 | 6.2 | 10.7
4 | 5.4 | 8.1 | 14
5.5 | 7.4 | 11 | 19
7.5 | 10 | 14.8 | 26
11 | 15 | 21 | 36
15 | 20 | 28.5 | 49
18.5 | 25 | 35 | 61
22 | 30 | 41 | 71
30 | 40 | 55 | 95
37 | 50 | 67 | 116
45 | 60 | 81 | 140
55 | 74 | 99 | 171
75 | 101 | 135 | 234
90 | 121 | 160 | 277
110 | 148 | 195 | 338
132 | 177 | 230 | 398
160 | 215 | 280 | 485
200 | 268 | 350 | 606
250 | 335 | 430 | 745
315 | 422 | 540 | 935
NEC table currents are for sizing conductors, fuses and breakers (430.6); set the overload relay from the nameplate. Cable sizes ignore voltage drop, grouping and ambient — check long runs with the voltage drop calculator and your local code. Source: https://tililt.com/charts/motor-current-chart/