## Minimum efficiency by class
Motor efficiency classes IE1–IE4 — Minimum efficiency by class — IEC 60034-30-1, 50 Hz (%)
kW | IE1 4p | IE2 4p | IE3 4p | IE4 4p | IE3 2p | IE3 6p
0.75 | 72.1 | 79.6 | 82.5 | 85.7 | 80.7 | 78.9
1.1 | 75 | 81.4 | 84.1 | 87.2 | 82.7 | 81
1.5 | 77.2 | 82.8 | 85.3 | 88.2 | 84.2 | 82.5
2.2 | 79.7 | 84.3 | 86.7 | 89.5 | 85.9 | 84.3
3 | 81.5 | 85.5 | 87.7 | 90.4 | 87.1 | 85.6
4 | 83.1 | 86.6 | 88.6 | 91.1 | 88.1 | 86.8
5.5 | 84.7 | 87.7 | 89.6 | 91.9 | 89.2 | 88
7.5 | 86 | 88.7 | 90.4 | 92.6 | 90.1 | 89.1
11 | 87.6 | 89.8 | 91.4 | 93.3 | 91.2 | 90.3
15 | 88.7 | 90.6 | 92.1 | 93.9 | 91.9 | 91.2
18.5 | 89.3 | 91.2 | 92.6 | 94.2 | 92.4 | 91.7
22 | 89.9 | 91.6 | 93 | 94.5 | 92.7 | 92.2
30 | 90.7 | 92.3 | 93.6 | 94.9 | 93.3 | 92.9
37 | 91.2 | 92.7 | 93.9 | 95.2 | 93.7 | 93.3
45 | 91.7 | 93.1 | 94.2 | 95.4 | 94 | 93.7
55 | 92.1 | 93.5 | 94.6 | 95.7 | 94.3 | 94.1
75 | 92.7 | 94 | 95 | 96 | 94.7 | 94.6
90 | 93 | 94.2 | 95.2 | 96.1 | 95 | 94.9
110 | 93.3 | 94.5 | 95.4 | 96.3 | 95.2 | 95.1
132 | 93.5 | 94.7 | 95.6 | 96.4 | 95.4 | 95.4
160 | 93.8 | 94.9 | 95.8 | 96.6 | 95.6 | 95.6
200+ | 94 | 95.1 | 96 | 96.7 | 95.8 | 95.8
Minimum nominal full-load efficiency for the class; a motor's catalogue figure is usually above it. 200+ = 200 kW up to 1000 kW. Regulation (EU) 2019/1781 sets which class may be sold; it has exemptions — check it before replacing a motor like for like. Source: https://tililt.com/charts/motor-efficiency-chart/

## EU Ecodesign
Motor efficiency classes IE1–IE4 — EU Ecodesign — what a new motor must be
Output | Minimum | Applies to
0.12–0.75 kW | IE2 | 2, 4, 6, 8-pole — since 1 Jul 2021
0.75–1000 kW | IE3 | 2, 4, 6, 8-pole — since 1 Jul 2021
75–200 kW | IE4 | 2, 4, 6-pole — since 1 Jul 2023
Ex eb motors | IE2 | 0.12–1000 kW — since 1 Jul 2023
Minimum nominal full-load efficiency for the class; a motor's catalogue figure is usually above it. 200+ = 200 kW up to 1000 kW. Regulation (EU) 2019/1781 sets which class may be sold; it has exemptions — check it before replacing a motor like for like. Source: https://tililt.com/charts/motor-efficiency-chart/