## Ambient temperature correction
Wire ampacity derating — Ambient temperature correction — factor by insulation rating
°C | °F | 60 °C | 75 °C | 90 °C
≤ 10 | ≤ 50 | 1.29 | 1.2 | 1.15
11–15 | 52–59 | 1.22 | 1.15 | 1.12
16–20 | 61–68 | 1.15 | 1.11 | 1.08
21–25 | 70–77 | 1.08 | 1.05 | 1.04
26–30 | 79–86 | 1 | 1 | 1
31–35 | 88–95 | 0.91 | 0.94 | 0.96
36–40 | 97–104 | 0.82 | 0.88 | 0.91
41–45 | 106–113 | 0.71 | 0.82 | 0.87
46–50 | 115–122 | 0.58 | 0.75 | 0.82
51–55 | 124–131 | 0.41 | 0.67 | 0.76
56–60 | 133–140 | — | 0.58 | 0.71
61–65 | 142–149 | — | 0.47 | 0.65
66–70 | 151–158 | — | 0.33 | 0.58
71–75 | 160–167 | — | — | 0.5
76–80 | 169–176 | — | — | 0.41
81–85 | 178–185 | — | — | 0.29
86–90 | 187–194 | — | — | —
Copper THHN/THWN-2 type wire. Factors computed with the method of NEC 2023 310.15(B) and (C)(1); 250 = 250 kcmil. 14, 12 and 10 AWG are still limited to 15, 20 and 30 A overcurrent protection. A starting point, not a design: check the code that applies to you. Source: https://tililt.com/charts/wire-ampacity-derating-chart/

## Adjustment for more than three
Wire ampacity derating — Adjustment for more than three current-carrying conductors
Conductors | Multiply by
4–6 | 80%
7–9 | 70%
10–20 | 50%
21–30 | 45%
31–40 | 40%
41 and up | 35%
Copper THHN/THWN-2 type wire. Factors computed with the method of NEC 2023 310.15(B) and (C)(1); 250 = 250 kcmil. 14, 12 and 10 AWG are still limited to 15, 20 and 30 A overcurrent protection. A starting point, not a design: check the code that applies to you. Source: https://tililt.com/charts/wire-ampacity-derating-chart/

## Derated copper ampacity, A
Wire ampacity derating — Derated copper ampacity, A — 90 °C wire on 75 °C terminals, 30 °C ambient
AWG | 1–3 | 4–6 | 7–9 | 10–20 | 4–6 at 40 °C
14 | 20 | 20 | 17 | 12 | 18
12 | 25 | 24 | 21 | 15 | 21
10 | 35 | 32 | 28 | 20 | 29
8 | 50 | 44 | 38 | 27 | 40
6 | 65 | 60 | 52 | 37 | 54
4 | 85 | 76 | 66 | 47 | 69
3 | 100 | 92 | 80 | 57 | 83
2 | 115 | 104 | 91 | 65 | 94
1 | 130 | 116 | 101 | 72 | 105
1/0 | 150 | 136 | 119 | 85 | 123
2/0 | 175 | 156 | 136 | 97 | 141
3/0 | 200 | 180 | 157 | 112 | 163
4/0 | 230 | 208 | 182 | 130 | 189
250k | 255 | 232 | 203 | 145 | 211
300k | 285 | 256 | 224 | 160 | 232
350k | 310 | 280 | 245 | 175 | 254
400k | 335 | 304 | 266 | 190 | 276
500k | 380 | 344 | 301 | 215 | 313
Copper THHN/THWN-2 type wire. Factors computed with the method of NEC 2023 310.15(B) and (C)(1); 250 = 250 kcmil. 14, 12 and 10 AWG are still limited to 15, 20 and 30 A overcurrent protection. A starting point, not a design: check the code that applies to you. Source: https://tililt.com/charts/wire-ampacity-derating-chart/