## Copper ampacity
Copper wire size — Copper ampacity (NEC 310.16)
AWG | mm² | 60 °C | 75 °C | 90 °C | OCPD max | Ω / 1000 ft
14 | 2.1 | 15 | 20 | 25 | 15* | 3.14
12 | 3.3 | 20 | 25 | 30 | 20* | 1.98
10 | 5.3 | 30 | 35 | 40 | 30* | 1.24
8 | 8.4 | 40 | 50 | 55 |  | 0.778
6 | 13.3 | 55 | 65 | 75 |  | 0.491
4 | 21.2 | 70 | 85 | 95 |  | 0.308
3 | 26.7 | 85 | 100 | 115 |  | 0.245
2 | 33.6 | 95 | 115 | 130 |  | 0.194
1 | 42.4 | 110 | 130 | 145 |  | 0.154
1/0 | 53.5 | 125 | 150 | 170 |  | 0.122
2/0 | 67.4 | 145 | 175 | 195 |  | 0.0967
3/0 | 85 | 165 | 200 | 225 |  | 0.0766
4/0 | 107 | 195 | 230 | 260 |  | 0.0608
250 kcmil | 127 | 215 | 255 | 290 |  | 0.0515
300 kcmil | 152 | 240 | 285 | 320 |  | 0.0429
350 kcmil | 177 | 260 | 310 | 350 |  | 0.0367
400 kcmil | 203 | 280 | 335 | 380 |  | 0.0321
500 kcmil | 253 | 320 | 380 | 430 |  | 0.0258
Copper, 75 °C terminations, not more than three current-carrying conductors. *14, 12 and 10 AWG are limited to 15, 20 and 30 A overcurrent protection (NEC 240.4(D)). A starting point, not a design: check the NEC and your local code. Source: https://tililt.com/charts/wire-size-chart/

## Copper size by load and one-way
Copper wire size — Copper size by load and one-way distance — 240 V, 1-phase, 3% drop
Load | 25 ft | 50 ft | 75 ft | 100 ft | 125 ft | 150 ft | 200 ft | 250 ft | 300 ft
15 A | 14 | 14 | 14 | 12 | 10 | 10 | 8 | 8 | 8
20 A | 12 | 12 | 12 | 10 | 10 | 8 | 8 | 6 | 6
30 A | 10 | 10 | 10 | 8 | 8 | 8 | 6 | 4 | 4
40 A | 8 | 8 | 8 | 8 | 6 | 6 | 4 | 4 | 3
50 A | 8 | 8 | 8 | 6 | 6 | 4 | 4 | 3 | 2
60 A | 6 | 6 | 6 | 6 | 4 | 4 | 3 | 2 | 2
70 A | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 1
80 A | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | 1/0
100 A | 3 | 3 | 3 | 3 | 3 | 2 | 1 | 1/0 | 2/0
125 A | 1 | 1 | 1 | 1 | 1 | 1 | 1/0 | 2/0 | 3/0
150 A | 1/0 | 1/0 | 1/0 | 1/0 | 1/0 | 1/0 | 2/0 | 3/0 | 3/0
175 A | 2/0 | 2/0 | 2/0 | 2/0 | 2/0 | 2/0 | 2/0 | 3/0 | 4/0
200 A | 3/0 | 3/0 | 3/0 | 3/0 | 3/0 | 3/0 | 3/0 | 4/0 | 250k
Copper, 75 °C terminations, not more than three current-carrying conductors. *14, 12 and 10 AWG are limited to 15, 20 and 30 A overcurrent protection (NEC 240.4(D)). A starting point, not a design: check the NEC and your local code. Source: https://tililt.com/charts/wire-size-chart/