## Register
Motor register |  |  | From https://tililt.com/workbooks/motor-register/ — rows 5–7 are examples: type over them. Grey columns work themselves out.
Motors |  | In service |  | Overdue |  | Due in 30 days |  | Installed kW
Where it is |  |  |  |  | Nameplate | [17 empty] | Bearings |  |  | Protection |  |  |  |  | Service
Tag | Location / line | Drives | Criticality | Status | Maker | Type / model | Serial no. | Power | Unit | kW | Volts | Amps (FLA) | Hz | rpm | Poles | Frame | Mounting | IP / enclosure | Ins. class | Efficiency | Duty | SF | DE bearing | NDE bearing | Grease | Starter | Overload set (A) | Overload check | Cable | Breaker / fuse | Installed | Last service | Every (months) | Next due | Due? | Notes
P-101 | Boiler house | Feed water pump 1 | A — stops production | In service | ABB | M3BP 132SMA 2 | 3GBP131210 | 5.5 | kW |  | 400Δ/690Y | 10.2 | 50 | 2915 |  | 132S | B35 | IP55 | F | IE3 | S1 | 1 | 6208-2Z/C3 | 6208-2Z/C3 | Sealed for life | DOL | 10.5 |  | 4×2.5 mm² | 16 A D-curve | 2021-03-15 | 2025-09-02 | 6 |  |  | Check alignment after any pump work.
F-204 | Cooling tower | Tower fan | B — slows production | In service | WEG | W22 180L | 1024887331 | 22 | kW |  | 400Δ | 40.5 | 50 | 1470 |  | 180L | V1 | IP56 | F | IE3 | S1 | 1.15 | 6311-C3 | 6211-C3 | Polyrex EM, 20 g / 4,000 h | VFD | 41 |  | 4×10 mm² SWA | 63 A gG | 2019-06-01 | 2026-04-20 | 6 |  |  | Regrease DE and NDE; VFD ramp 15 s.
C-310 | Line 3 | Infeed conveyor | C — can wait | Spare on shelf | Baldor | EM3615T | F1905220314 | 5 | HP |  | 230/460 | 6.2 | 60 | 1750 |  | 184T | NEMA T (feet) | TEFC | F | NEMA Premium | S1 | 1.15 | 6206-2Z/C3 | 6205-2Z/C3 | Sealed for life | DOL | 9 |  | 12 AWG THHN | 15 A | 2022-11-08 | 2024-11-08 | 12 |  |  | Shelf spare for C-301 to C-312. Overload was set for 230 V wiring — reset to 460 V FLA before fitting.
Formulas:
Next due = IF(OR([Last service]="",[Every (months)]=""),"",EDATE([Last service],[Every (months)]))
Due? = IF([Next due]="","",IF([Next due]<TODAY(),"Overdue",IF([Next due]-TODAY()<=30,"Due in 30 days","OK")))

## Spares
Bearing spares
List the bearings you stock. 'Used on' counts the motors in the register that take each one, at either end.
Bearing | On the shelf | Keep at least | Used on (motors) | Reorder?
6208-2Z/C3 | 2 | 2
6311-C3 | 1 | 1
6211-C3 | 0 | 1
6206-2Z/C3 | 1 | 1
6205-2Z/C3 | 1 | 1

## Lists
Criticality | Status | Unit | Hz | Mounting | IP | Insulation | Efficiency | Duty | Starter
A — stops production | In service | kW | 50 | B3 | IP23 | B | IE1 | S1 | DOL
B — slows production | Spare on shelf | HP | 60 | B5 | IP44 | F | IE2 | S2 | Star-delta
C — can wait | Out for repair |  |  | B14 | IP54 | H | IE3 | S3 | Soft starter
| Retired |  |  | B35 | IP55 |  | IE4 | S4 | VFD
|  |  |  | B34 | IP56 |  | IE5 | S6 | Reversing DOL
|  |  |  | V1 | IP65 |  | NEMA Premium | S9 | Two-speed
|  |  |  | V5 | IP66 |  | Unknown
|  |  |  | V18 | ODP
|  |  |  | NEMA T (feet) | TEFC
|  |  |  | NEMA TC (C-face) | TENV
|  |  |  | NEMA TD (D-flange) | XP
Add your own entries under any heading, down to row 40; the drop-downs in the register pick them up.

## How to fill it
How to fill in the register
One line per motor, including the spares on the shelf. Only the tag is needed to start; fill in the rest the next time you are at the motor.
Column | Group | What to put in it
Tag | Where it is | Your own number, painted on the motor or the plant drawing. Keep it unique — a planner uses it to tell the motors apart.
Location / line | Where it is | Building, area or line.
Drives | Where it is | The machine it turns: pump, fan, conveyor, compressor.
Criticality | Where it is | A if its failure stops production. A motors are the ones to keep a spare for.
Status | Where it is | In service, on the shelf, away for rewind, or retired.
Maker | Nameplate | Top of the plate.
Type / model | Nameplate | Type or catalogue number — the most useful line when you order a like-for-like.
Serial no. | Nameplate | What the maker asks for under warranty.
Power | Nameplate | Rated output at the shaft, as printed.
Unit | Nameplate | kW or HP. The kW column converts HP for you so the register sorts and sums.
kW | Nameplate | Calculated.
Volts | Nameplate | As printed, e.g. 400Δ/690Y or 230/460.
Amps (FLA) | Nameplate | Full-load current at the voltage it is actually connected for.
Hz | Nameplate | 50 or 60.
rpm | Nameplate | Full-load speed from the plate.
Poles | Nameplate | Calculated from rpm and Hz: 2,900 rpm at 50 Hz is 2-pole, 1,450 is 4-pole.
Frame | Nameplate | IEC (132S, 180L) or NEMA (184T). Same frame, same foot holes and shaft.
Mounting | Nameplate | Feet, flange or both.
IP / enclosure | Nameplate | IP rating, or the NEMA enclosure (TEFC, ODP).
Ins. class | Nameplate | Insulation class, usually F.
Efficiency | Nameplate | IE class or NEMA Premium. Check the EU rules before a like-for-like replacement.
Duty | Nameplate | S1 is continuous; anything else means the motor was sized for stop-start.
SF | Nameplate | Service factor, on NEMA plates. 1.0 if none is given.
DE bearing | Bearings | Drive-end bearing, often on the plate or the grease nipple tag.
NDE bearing | Bearings | Non-drive-end bearing.
Grease | Bearings | Type and quantity, or 'sealed for life'.
Starter | Protection | How it is started.
Overload set (A) | Protection | What the overload relay is set to.
Overload check | Protection | Calculated: flags a relay set more than 25% above the plate current, or more than 10% below it.
Cable | Protection | Size and type of the supply cable.
Breaker / fuse | Protection | Breaker or fuse protecting the circuit.
Installed | Service | Date fitted.
Last service | Service | Date of the last planned service.
Every (months) | Service | Service interval in months.
Next due | Service | Calculated: last service + interval.
Due? | Service | Calculated: Overdue, Due in 30 days, or OK.
Notes | Service | Anything the next person should know.
Help with the plate
Reading the plate, line by line
Choosing a replacement motor
IEC frame sizes
NEMA frame sizes
Motor current and cable